## Slide 1: Princibles of wind power

## Slide 7: Optimization of selecting aerofoil

## Slide 8: Types of aerofoil used in HAWT
BLADE LENGTH (meter) | Generator size (KW) | THICKNESS CATEGORY | (root -------- | AIRFOIL ---------------- | FAMILY ----------------- | ------tip)
1-5 | 2-20 | thick |  | S823 |  | S822
5-10 | 20-150 | thin |  | S804 | S801 | S803
5-10 | 20-150 | thin | S808 | S807 | S805A | S806A
5-10 | 20-150 | thick |  | S821 | S819 | S820
10-15 | 150-400 | thick | S815 | S814 | S809 | S810
10-15 | 150-400 | thick | S815 | S814 | S812 | S813
15-25 | 400-1000 | thick |  | S818 | S816 | S817

## Slide 9: NREL aerofoils National Renewable Energy Laboratory

## Slide 10
Blades 1 to 5 Meters in Length One airfoil family, which consists of a root airfoil (S823) and tip airfoil (S822), was designed in 1993 for small turbines rated at 2-20 kW. The design specifications for this family indicate a tip region Cl of 1. 0 and a minimum drag Cd,min of 0. 010 for a Reynolds number of 600,000. The very
low Reynolds number range for this family contnoutes to a higher cd,min and increased difficulty in achieving a high root airfoil Cl max (1.2) for a Reynolds number of 400,000. This airfoil family is
suitable for many small variable-rpm machines such as the Jacobs 17.5 kW machine.

## Slide 15: Energy extraction
The energy extraction is maintained in a flow process through the reduction of kinetic energy and subsequent velocity of the wind
The magnitude of energy harnessed is a function of the reduction in air speed over the turbine
100% extraction would imply zero final velocity and therefore zero flow,and this scenario can’t be achieved hence all the wind kinetic energy may not be utilized

## Slide 16: Blades efficiency

## Slide 17
Betz limit theory says that max. efficiency of a wind turbine is 59.3%
Betz theory assumption is that the flow is constant and linear
High ratio of Cl/Cd means higher power coefficient and high efficiency
Efficiency losses are generally reduced by:
-avoiding low tip speed ratios which increase wake rotation
-selecting an airfoils which have a high lift to drag ratio

## Slide 19: Some important geometry factors affecting the design
NO.of blades
Blade shape
We have a challenge that we want a thinner blades V.S blades with good structural strength
The more NO. OF BLADES ,The more the efficiency and the more the cost
From 2 blades to 3 blades the efficiency increases 3%
From 3 blades to 4 blades the efficiency increases only 0.5%

## Slide 20
Blade length
Power =0.5*efficiency*Rho*A*V^3
The proplems are:
-over deflection for blade
-proplem of noise
-heavy investment
TOWER height
The more the altitude”hight”,the more the speed of wind and the more the power gained

## Slide 21: Flow chart of simulation